SPECIFICATIONS FOR MINI SIMPLEX SYSTEM

Furnish and install a Model ____________ Mini Simplex constant speed, variable flow factory assembled water booster system as manufactured by Canariis Corporation, Riverview, Florida.  The unit shall be rated for a system capacity of _____ GPM, with a system pressure of _____ PSIG, including a minimum suction pressure of _____ PSIG.  Maximum suction pressure will be _____ PSIG.

FACTORY ASSEMBLY

The booster system shall be factory assembled including pump, motor, valve, tank, discharge pressure gauge, thermal purge valve and controls. All components shall be factory finished in a high quality enamel paint.

Components shall be suitable for the maximum working pressure in the system.

PUMP AND MOTOR

System shall include one horizontal mounted close-coupled end suction centrifugal pump with ANSI flanged connections.  Pump features to include foot supported casing, back pull out design, top centerline discharge and hydraulically balanced impeller.  Pump shall be cast iron bronze fitted construction with a replaceable shaft sleeve and mechanical seal suitable for a working pressure of 175 PSIG.

Pump shall be rated _____ GPM at _____ ft head.

Motor shall be _____ volt, _____ phase, _____ Hz, (open drip proof) (totally enclosed fan cooled) NEMA close-coupled type with a JM shaft and shall be _____ HP, _____ RPM.

SYSTEM VALVE

Pump will have a silent non-slam check valve sized for a maximum loss of 3 PSI at design flow and shall be suitable for the maximum working pressure of the system.

HYDRO-PNEUMATIC TANK

System shall include a 5.0 gallon hydro-pneumatic tank suitable for a working pressure up to 150 PSIG.

PUMP OPERATION

The pump shall run only as necessary to maintain system pressure and will be controlled automatically by means of a pressure switch and minimum run timer to prevent short cycling.

CONTROL PANEL

Each system shall include a UL listed enclosed industrial control panel in a NEMA 1 enclosure, factory mounted and wired.  The panel shall be furnished with a main disconnect, fusing, magnetic starter with (3) leg overload protection, pump run light, H-O-A selector switch, 115 volt fused control transformer, timer and pump start/stop pressure switch.

FACTORY TEST

After factory assembly, the packaged pumping system shall be hydrostatically tested as well as undergo a complete electric and hydraulic test from 0 to 100% design flow at the factory.  All controls, pump sequencing devices, alarms and instrumentation shall be tested and calibrated for proper operation during factory testing.

WARRANTY

The booster system shall be warranted in writing against defects in materials or workmanship under normal use and service for a period of one year after date of original operation but not more than 18 months from date of shipment from the Company's factory, when installed and used in accordance with good standard practice.