SPECIFICATIONS FOR SIMPLEX SYSTEMS

Furnish and install a Model ____________ Simplex constant speed, variable flow factory assembled water booster system as manufactured by Canariis Corporation, Riverview, Florida.  The unit shall be rated for a system capacity of _____ GPM, with a system pressure of _____ PSIG, including a minimum suction pressure of _____ PSIG.  Maximum suction pressure will be _____ PSIG.

The complete Packaged Pumping System, including pump, motor, control equipment, tank, valves, and fittings must be UL Listed under Category QCZJ (Packaged Pumping Systems).  In addition to the UL Listing for the complete system the control panel assembly must be separately listed under UL 508A (Industrial Control Panels). All welding shall be performed by certified welders in accordance with ASME section IX.

FACTORY ASSEMBLY

The booster system shall be factory assembled on a steel skid including pump, motor, valve, and all interconnecting piping, wiring and controls.  Provide one 4 1/2" ASME grade A, gauge for indicating system discharge pressure. A thermal purge valve shall be provided on the discharge of the pump.  All skid mounted components shall be factory finished in a high quality enamel paint.  Components shall be suitable for the maximum working pressure in the system.

PUMPS

System shall include one horizontal mounted close-coupled end suction centrifugal pump with ANSI flanged connections.  Pump features to include foot supported casing, back pull out design, top centerline discharge and hydraulically balanced impeller.  Pump shall be cast iron bronze fitted construction with a replaceable shaft sleeve and mechanical seal suitable for a working pressure of 175 PSIG.

Pump shall be rated _____ GPM at _____ ft head.

MOTOR

Motor shall be _____ volt, _____ phase, _____ Hz (open drip proof) (totally enclosed fan cooled) manufactured in accordance with NEMA close-coupled standards with a JM shaft and shall be _____ HP, _____ RPM.

SYSTEM VALVE   (choose A or B)

Option A:

Constant system pressure shall be maintained by a pilot-operated diaphragm type combination pressure regulating and non-slam check valve.  Main valve and cover shall be ductile iron with a fused epoxy coating and stainless steel stem and cover bolts.  Construction shall be suitable for the maximum working pressure of the system.

Option B:

Pump discharge shall have a silent, non-slam check valve sized for a maximum loss of 3 PSI at design flow and be suitable for the maximum working pressure of the system.

(If hydro-pneumatic tank is required include the following)

HYDRO-PNEUMATIC TANK

Provide a hydro-pneumatic tank with a carbon steel shell and a replaceable F.D.A. approved heavy duty bladder to separate the air and water.  No water shall come in contact with the metal walls of the tank.  Features shall include an air fill valve and bottom system connection suitable for 100% drawdown.

Tank size and rating (choose A or B)

Option A:

The tank must be suitable for a maximum working pressure of 150 PSIG with a volume of (80) (132) (198) gallons.

Option B:

The tank must be constructed in accordance with Section VIII of the ASME code and be N.B. stamped and shall be rated (79 gallon - 125 PSIG) (106 gallon - 125 PSIG) (132 gallon - 125 PSIG) (158 gallon - 125 PSIG) (211 gallon - 125 PSIG) (185 gallon - 200 PSIG).

Tank mounting arrangement (choose A or B)

Option A:

The tank shall be mounted (adjacent to the system requiring one field connection) (on the pump skid), and the tank feed line shall be connected between the pump discharge and its PRV to provide maximum tank storage.

Option B:

The tank shall be mounted in a remote location as shown on the drawings.

PUMP OPERATION

Option A:

The pump shall run only as necessary to maintain system pressure and shall be controlled automatically by means of a pressure switch and minimum run timer to prevent short cycling.

Option B:

The pump shall run continuously and shall be protected from overheating by a thermal purge valve.

CONTROL PANEL

Each system shall include a UL listed enclosed industrial control panel in a NEMA 1 (NEMA 12, 3R) enclosure factory mounted and wired on the steel skid.  The panel shall be furnished with (one main disconnect with three power fuses) (main disconnect with circuit breaker) with through the door handle, magnetic starter with (3) leg overload protection, pump run light, H-O-A selector switch, 115 volt fused control transformer, necessary relays and timers or a programmable logic controller and pump start, stop and sequence controls.

Control Panel Options  (choose features required)

In addition the control panel shall be furnished with the following features:

 THRU THE DOOR RESET BUTTON

 MOTOR O/L INDICATING LIGHT

 CONTROL POWER (ON-OFF) SWITCH AND LIGHT

 LOW SUCTION PRESSURE SHUTDOWN CIRCUIT WITH AUTO RESET, DELAY TIMER AND LIGHT

 LOW SUCTION LEVEL SHUTDOWN CIRCUIT WITH AUTO RESET AND LIGHT – (SIGNAL BY OTHERS)

 HIGH SUCTION PRESSURE SHUTDOWN CIRCUIT WITH AUTO RESET, DELAY TIMER AND LIGHT

 HIGH SYSTEM PRESSURE SHUTDOWN CIRCUIT WITH MANUAL RESET AND LIGHT

 AUDIBLE ALARM WITH SILENCE PUSH BUTTON

 7 DAY TIME CLOCK FOR INTERMITTENT SYSTEM OPERATION

 FLOW SWITCH TO LIMIT PUMP ON-OFF CYCLING

 ELAPSED TIME METER

 REMOTE ALARM PANEL WITH SILENCE PUSH BUTTON AND LIGHT

 AUXILIARY RELAY CONTACTS

 PHASE LOSS, LOW/HIGH VOLTAGE SHUTDOWN WITH AUTO RESET AND LIGHT

 KEY LOCKABLE ENCLOSURE

 PROGRAMMABLE LOGIC CONTROLLER (PLC)

 LIGHTNING ARRESTER



FACTORY TEST

After factory assembly, the packaged pumping system shall be hydrostatically tested and shall undergo a complete electric and hydraulic test from 0 to 100% design flow at the factory.  All controls, pump sequencing devices, alarms and instrumentation shall be tested and calibrated for proper operation during factory testing.

WARRANTY

The booster system shall be warranted in writing against defects in materials or workmanship under normal use and service for a period of one year after date of original operation but not more than 18 months from date of shipment from the Company's factory when installed and used in accordance with good standard practice.

START-UP SERVICE

The service of a factory trained representative shall be made available on the jobsite for start-up and instructing operating personnel.