SPECIFICATIONS FOR

DUPLEX VARIABLE SPEED SYSTEMS

Furnish and install a Model ____________ Duplex variable speed, variable flow factory assembled water booster system as manufactured by Canariis Corporation, Riverview, Florida.  The unit shall be rated for a system capacity of _____ GPM, with a system pressure of _____ PSIG, including a minimum suction pressure of _____ PSIG.  Maximum suction pressure will be _____ PSIG.

The complete Packaged Pumping System, including pumps, motors, control equipment, variable frequency drives, tank, valves, fittings and manifolds must be UL Listed under Category QCZJ (Packaged Pumping Systems).  In addition to the UL Listing for the complete system the control panel assembly must be separately listed under UL 508A (Industrial Control Panels). All welding shall be performed by certified welders in accordance with ASME section IX.

FACTORY ASSEMBLY

The booster system shall be factory assembled on a steel skid including pumps, motors, valves, _____" (SCH40 steel hot-dip galvanized after fabrication) (type "L" copper) (SCH10 300 series stainless steel) suction and discharge manifolds, and all interconnecting piping, wiring and controls. Manifold connections will be (grooved) (flanged) at one end. Branch piping and tank piping (if applicable) shall be the same material as the suction and discharge manifolds.  Provide isolation valves on the suction and discharge of each pump.  The valves shall be (full-port ball valves) (lug style butterfly valves). Provide a thermal purge valve on the discharge of each pump. Provide two 4 1/2" ASME grade A, panel mounted gauges for indicating system suction and system discharge pressure.  All skid mounted components shall be factory finished in a high quality enamel paint.

Individual pumps, motors and pressure regulating or check valves may be serviced with the booster system in operation and all components shall be suitable for the maximum working pressure and temperature in the system.

PUMPS (choose A or B)

Option A:

System shall include two horizontal mounted close-coupled end suction centrifugal pumps with ANSI flanged connections.  Pump features to include foot supported casing, back pull out design, top centerline discharge and hydraulically balanced impeller.  Pump shall be cast iron bronze fitted construction with a replaceable shaft sleeve and mechanical seal suitable for a working pressure of 175 PSIG.  Motor shall be NEMA close-coupled type with a JM shaft.

Option B:

System shall include two multi-stage vertical centrifugal pumps with ANSI flanged connections.  The pump suction/discharge chamber, motor stool and pump shaft coupling shall be constructed of cast iron.  The impellers, pump shaft, diffuser chambers, outer discharge sleeve and impeller seal rings or seal ring retainers shall be constructed of stainless steel.  Intermediate and lower shaft bearings shall be bronze or tungsten carbide and ceramic.  Pumps shall be equipped with a mechanical seal assembly with tungsten carbide seal faces mounted in stainless steel seal components.  The pump motor shall be NEMA C face design mounted directly to the top of the pump.

Pump No. 1 and Pump No. 2 shall be rated _____ GPM at _____ ft head.

MOTORS

Motors shall be _____ volt, _____ phase, _____ Hz (open drip proof) (totally enclosed fan cooled) and manufactured in accordance with NEMA standards.  Pump No. 1 and Pump No. 2 shall be _____ HP, _____ RPM.  Motors shall be selected so that they do not exceed nameplate HP rating throughout the programmed sequence of pump operation.

SYSTEM VALVES  (choose A or B)

Option A: (Use this option if bypass starters are provided)

Over pressurization of the system while operating across-the-line shall be prevented by a pilot operated diaphragm type combination pressure regulating and non-slam check valve on each pump.  Main valve and cover shall be ductile iron with a fused epoxy coating and stainless steel stem and cover bolts.  Construction shall be suitable for the maximum working pressure of the system.

Option B: (Use this option if bypass starters are not provided)

Each pump discharge shall have a wafer style silent non-slam check valve with cast iron body and sized for a maximum loss of 3 PSI at design flow and be suitable for the maximum working pressure of the system.

(If hydro-pneumatic tank is required include the following)

HYDRO-PNEUMATIC TANK

Provide a hydro-pneumatic tank with a carbon steel shell and a replaceable F.D.A. approved heavy duty bladder to separate the air and water.  No water shall come in contact with the metal walls of the tank.  Features shall include an air fill valve and bottom system connection suitable for 100% drawdown.

Tank size and rating (choose A or B)

Option A:

The tank must be suitable for a maximum working pressure of 150 PSIG with a volume of (80) (132) (198) gallons.

Option B:

The tank must be constructed in accordance with Section VIII of the ASME code and be N.B. stamped and shall be rated (79 gallon – 125 PSIG) (106 gallon - 125 PSIG) (132 gallon - 125 PSIG) (158 gallon - 125 PSIG) (211 gallon - 125 PSIG) (185 gallon - 200 PSIG).

Tank mounting arrangement (choose A or B)

Option A:

The tank shall be mounted (adjacent to the system requiring one field connection) (on the pump skid),        and the tank feed line shall be connected between the lead pump(s) discharge and its PRV to provide maximum tank storage.

Option B:

The tank shall be mounted in a remote location as shown on the drawings.

VARIABLE FREQUENCY DRIVES

Provide and mount on the system skid two variable frequency drives of the PWM design suitable for variable torque applications using any standard NEMA Design B squirrel cage induction motor.  Variable frequency drives shall sized for the maximum possible amp draw throughout the programmed sequence of pump operation.

Standard Features

Pulse Width Modulated

Starts into a rotating load

Keypad Operator Device including the following:

2 Line Backlit LCD Display

Power On and Alarm/Fault Displays

In Auto the drive follows signal from Logic Section of Control Panel

Hand/off/auto switch and manual speed adjustment

Auto Drive Shutdown for electrical fault

Automatic restart after power fails shutdown

Operational data displays include: Drive Speed (HZ), Motor Power, Energy (kWh), Current, Elapsed Time, RPM, and Motor Voltage

Complete Service Diagnostics with fault history log.

The efficiency at full load and full speed will be 97% with a fundamental power factor of .98.

(If the VFDs require bypasses include the following)

VARIABLE FREQUENCY DRIVE BYPASSES

Each VFD bypass will include

Door interlocked circuit breaker

One motor overload relay

2 contactor bypass

Drive-off-bypass switch

Drive and bypass pilot lights

UL listed

PRESSURE SENSOR/TRANSMITTER

Provide one pressure sensor/transmitter that provides a 4 to 20 mA DC output, compatible with the system controls, temperature and pressure requirements.  Pressure sensor/transmitter shall have zero, span and damping devices.  The transmitter shall be installed on the system discharge header and factory wired to the control panel.

SEQUENCE OF OPERATION (Choose A or B)

Option A:

The lead pump shall run only as necessary to maintain system pressure and will be controlled automatically by means of a pressure sensor/transmitter and programmable logic controller (PLC) programmed to prevent short cycling.  If the lead pump is unable to maintain system pressure the lag pump will be called on after a time delay and will operate in parallel with the lead pump in accordance with the PLC program.  When one pump can handle the system demand the controls will shut down the lag pump.  When a low or no flow condition is reached, the controls will accelerate the lead pump to charge the system and hydro-pneumatic tank then shut the lead pump down and alternate.

Option B:

The lead pump shall run continuously to maintain system pressure and will be controlled automatically by means of a pressure sensor/transmitter and programmable logic controller.  If the lead pump is unable to maintain system pressure the lag pump will be called on after a time delay and will operate in parallel with the lead pump in accordance with the PLC program.  When one pump can handle the system demand the controls will shut down the lag pump. Pump alternation is accomplished with a 24-hour time clock.

CONTROL PANEL

Logic Section

Provide, mount and wire on the skid a programmable logic controller in an enclosure to interface the signal from the pressure sensor to the VFD's and provide a stabilized response to speed up or slow down the pump or add the lag pump to meet system requirements.  The controller shall provide setpoint adjustment, timer adjustment, PID functions and both system and controller self diagnostics via a 2 line 20 character display with keypad (5.7” STN touchscreen display).  All user interface setpoints are easily accessible via the password protected display screen.  Normal system operation is tuned to eliminate hunting.  Controller shall have one RS 485 Communication port, real time calendar/clock and EEPROM memory transfer cartridge.

Power Section

Each system shall include a UL listed enclosed industrial control panel in a NEMA 1 (NEMA 12, 3R) enclosure, factory mounted and wired on the steel skid.  The panel shall be furnished with individual pump disconnects with through the door handles, pump run lights, H-O-A selector switches and 115 volt fused control transformer.

STANDARD CONTROL PANEL FEATURES

  UL LISTED ENCLOSED INDUSTRIAL CONTROL PANEL

  INDIVIDUAL FUSED DISCONNECTS WITH EXTERNAL HANDLE

  PROGRAMMABLE LOGIC CONTROLLER  (PLC)

  PUMP RUNNING LIGHTS

  H/O/A SELECTOR SWITCHES

  115 VOLT FUSED CONTROL CIRCUIT TRANSFORMER

  PUMP MINIMUM RUN TIMERS

  MOUNTED AND WIRED ON SKID

  PUMP OPERATING AND SEQUENCE CONTROLS

CONTROL PANEL OPTIONS

  CONTROL POWER (ON-OFF) SWITCH AND LIGHT

  LOW SUCTION PRESSURE SHUTDOWN CIRCUIT WITH AUTO RESET, DELAY TIMER AND LIGHT

  LOW SUCTION LEVEL SHUTDOWN CIRCUIT WITH AUTO RESET AND LIGHT – (SIGNAL BY OTHERS)

  LOW SYSTEM PRESSURE CIRCUIT TO START STANDBY PUMP(S) WITH MANUAL RESET AND LIGHT

  HIGH SUCTION PRESSURE SHUTDOWN CIRCUIT WITH AUTO RESET, DELAY TIMER AND LIGHT

  HIGH SYSTEM PRESSURE SHUTDOWN CIRCUIT WITH MANUAL RESET AND LIGHT

  AUDIBLE ALARM WITH SILENCE PUSH BUTTON

  AUTO ALTERNATE (2) EQUAL PUMPS

  24 HOUR TIME CLOCK - ALTERNATE (2) EQUAL PUMPS

  7 DAY TIME CLOCK FOR CONTINUOUS SYSTEM OPERATION

  FLOW SWITCH TO LIMIT LEAD PUMP ON-OFF CYCLING

  ELAPSED TIME METERS

  REMOTE ALARM PANEL WITH SILENCE PUSH BUTTON AND LIGHT

  AUXILIARY RELAY CONTACTS

  KEY LOCKABLE ENCLOSURE

  LIGHTNING ARRESTER

  EMERGENCY POWER ALARM TO PREVENT LAG PUMP OPERATION (SIGNAL BY OTHERS)





#### FACTORY TEST

The booster system shall be hydrostatically tested and shall undergo a complete electric and hydraulic test from 0 to 100% design flow at the factory.  All control devices including transmitters and all safety features shall be factory calibrated and tested.  The owner’s representative may witness the test.

WARRANTY

The booster system shall be warranted in writing against defects in materials or workmanship under normal use and service for a period of one year after date of original operation but not more than 18 months from date of shipment from the Company's factory when installed and used in accordance with good standard practice.

START-UP SERVICE

The service of a factory-trained representative shall be made available on the jobsite for start-up and instructing operating personnel.